## 新华联资源赞比亚公司

## MACROLINK RESOURCES ZAMBIA LIMITED

Mwekera Copper Mine, Ndola, Copperbelt Province, Zambia                             Email: macrolinkresources@gmail.com

Phone Number: 0969-598313 / 0973 -701968

TENDER NOTICE

17/08/2026

Tender No. MRZTND263-0014

SUPPLY AND DELIVERY OF MEDIUM VOLTAGE CABLE ACCESSORIES

Our Company invites sealed tenders from eligible manufacturers or authorized distributors for the supply and delivery of high-quality **11kV 3-Core 35mm² Termination Kits**. The required kits must provide exceptional electrical insulation, environmental sealing, and mechanical protection for indoor or outdoor Medium Voltage (MV) power distribution networks. 2. Technical Specification

Technical Specifications

All materials supplied under this contract must strictly adhere to international standards (e.g., IEC 60502-4, IEEE 48, BS 7888) and meet the following minimum parameters:

• Voltage Rating: 11kV (Uo/U = 6.35/11kV up to 12kV maximum system voltage).

• Cable Application: Designed for 3-Core, 35mm² copper or aluminum XLPE/PVC insulated, armored (SWA) or unarmored power cables.

• Technology: Heat-shrinkable or cold-shrinkable type, complete with anti-tracking, stress-control tubes, and environmental sealing rain sheds.

• Breakout Boot: Heavy-duty, track-resistant molded 3-way breakout boot pre-coated with hot-melt adhesive seal.

• Lug Kit: Includes matching mechanical shear-bolt or compression lugs suitable for 35mm² conductors. • Earthing System: Must include a complete earthing kit (tinned copper braid, constant force springs, and armor clamps) for armor/shield continuity.

Eligibility Requirements

Bidders must meet the following requirements:

- Be a legally registered company with valid business licenses;

- Have relevant experience in supplying similar products, preferably in the mining sector;

- Possess good commercial reputation with no record of major violations;

- Have the capacity to ensure timely delivery and provide after-sales support;

- Be able to issue valid invoices and provide product quality certifications.

Tender Submission

Bidders shall submit their proposals before the submission deadline. Late submissions will not be accepted.

Additional Information

The tender will be evaluated based on a comprehensive assessment;

The Company reserves the right to accept or reject any bid without assigning any reason;

Further details will be provided upon request.

Submission Deadline: [17/08/2026]

Contact:   Mr. Lewis

Email:       macrolinkresources@gmail.com

Phone:     0969-598313

MACROLINK RESOURCES ZAMBIA LIMITED

Date: 17/08/2026